Willowglen Services Pte Ltd

103 Defu Lane 10, #05-01
Singapore 539223
Tel: (65) 62800437
Fax: (65) 62862002

Supply, Design, Installation and Commissioning of Supervisory Control and Data Acquisition (SCADA) and Telemetry System for Public Utilities Board Water Supply Network System

# Cybersecurity Plan

Project No			：	1547

Document No			:	1547_CSP

Revision No.			:	V1

Contents

1.	Abbreviations	4

2.	dObjectives	5

3.	References	5

4.	Scope	5

5.	Cybersecurity Activities and Deliverables	5

6.	Security Roles & Responsibilities	6

6.1	Security Planning and Risk Assessment	6

6.2	Critical Security Design Review	7

6.3	System Security Acceptance Test	7

6.4	Vulnerability Assessment and Penetration Testing	7

6.5	Patch and Vulnerability Management	8

6.6	Cybersecurity Design requirements	8

6.6.1	Asset Management	8

6.6.2	Account Management	9

6.6.3	Password Policy	10

6.6.4	Access Control	10

6.6.5	Privileged Access	11

6.6.6	Zero Trust framework	11

6.6.7	Remote Access	12

6.6.8	Network Segmentation	13

6.6.9	Network security	14

6.6.10	Data Security	14

6.6.11	Endpoint Security	15

6.6.12	Application Security	15

6.6.13	Physical Security	16

6.6.14	System Hardening	16

6.6.15	Obsolescence Management	19

6.6.16	Logging	20

6.7	Security Acceptance Test	21

6.8	Recovery	21

6.8.1	Backup and Restoration Plan	21

6.8.2	BUSINESS CONTINUITY AND DISASTER RECOVERY PLAN	22

6.9	Cybersecurity Incident Management	23

6.10	3rd party Cybersecurity Risk Management	24

7.	Vulnerability Assessment and Penetration Testing (VAPT)	24

7.1	Vulnerability Assessment	24

7.2	Penetration Testing	25

7.3	VAPT Steps	25

7.4	TIMING & FREQUENCY	26

Appendix A Document List	27

|  | NAME | APPOINTMENT | SIGNATURE |
| --- | --- | --- | --- |
| PREPARED BY |  |  |  |
| CHECKED BY |  | Cyber Security Manager |  |
| VERIFIED BY |  | Cybersecurity Consultant |  |
| APPROVED BY |  |  |  |

| Primary Author(s) | Description | Revision | Date |
| --- | --- | --- | --- |

# Abbreviations

| Abbreviation | Definition |
| --- | --- |
| WSPL | Willowglen services private limited |
| CCoP 2.0 | Cybersecurity Code of Practice for CII |
| CSF | Cybersecurity Framework |
| DNS | Domain Name System |
| HMI | Human Machine Interfaces |
| NIDS/NIPS | Network Intrusion Detection/Prevention System |
| RMF | Risk Management Framework |
| RR | Risk Registry |
| VAPT | Vulnerability Assessment and Penetration Testing |
| CSA | Cyber Security Agency of Singapore |
| NIST | National Institute of Standards and Technology (NIST) |
| NIST CSF | NIST Cybersecurity Framework |
| CII | Critical Information Infrastructure |
| WSCP | Water Sector Cybersecurity Policy |
| RBAC | Role-Based Access Control |
| MFA | Multi-Factor Authentication |
| IT | Information Technology (Enterprise) |
| ITSM | IT Security Manager |
| OMM | Operation and Maintenance Manual |
| SSAT | System Security Acceptance Test |
| WSN | Water Supply Network |

# Objectives

This documentation is developed in accordance with the guidelines established in Supply, Design, Installation and Commissioning of Supervisory Control and Data Acquisition (SCADA) and Telemetry System for Public Utilities Board Water Supply Network System specifications. It contains information proposed for the cybersecurity implementation that involved parties in the project to protect PUB information technology systems and data.

This document provides guidance, instructions and required format for the WSN project. The security plan, guidelines and instructions apply to all entities implementing this project.

This document detailed technical implementation, which adopted relevant international standards and best practices

# References

- WATER SUPPLY (NETWORK) DEPARTMENT TECHNICAL SPECIFICATIONS

- PUB’s Water Sector Cybersecurity Policy (WSCP) V3.2

- CSA’s Cybersecurity Code of Practice (CCoP 2) V2.1

# Scope

This document will

- Provide clear scope of cybersecurity supply for the project implementation

- Identify cybersecurity mandatory requirements

- Document each step in the cybersecurity lifecycle has been verified as complete

- Document required project communication with project team members and PUB

# Cybersecurity Activities and Deliverables

| SN | SBD Phase | Tender Cybersecurity Requirements | Deliverables |
| --- | --- | --- | --- |
| 1 | Initiation |  | - Cybersecurity Plan - ICT Asset Inventory List (Hardware & Software) - Security-by-Design (SBD) Checklist |
| 2 | Design and Development | - Scope of Work - Technical Specification - Review Security Controls - Review Security Architecture | - Threat & Risk Assessment Report - System Security Design Spec - System Security Review Report (Architect and Control) |
| 3 | Implementation / Assessment | - Testing and Commissioning - Threat & Risk Assessment | - Security Source Code Review Report - Hardening Standard and Guideline - Hardening Report - Configuration Report - Switch Port Whitelisting - Patching Method of Statement (MOS) - Patch Record - SSAT Plan - SSAT Report |
| 4 | Implementation / Assessment | - Perform Vulnerability Assessment and Penetration Testing | - VAPT Method of Statement (MOS) - VAPT Report |
| 5 | Post-Implementation | - Establish Incident Handling, Continuity and Recovery Capabilities | - Incident Response Plan - Business Continuity Plan (BCP) - Disaster Recovery Plan (DRP) - Crisis Communication Plan |

Table 3 Cybersecurity Activities and Deliverables

# Security Roles & Responsibilities

Via reference to CSA Security-by-Design framework, the following are the roles and responsibilities define for

- Security Planning

- Design Review

- System Security Acceptance Test

- Patch and Vulnerability Management

## Security Planning and Risk Assessment

| Roles | Responsibilities | Company |
| --- | --- | --- |
| Project Manager | The Project Manager is responsible to ensure that the security planning and risk assessment are performed adequately and completed and all inputs from stakeholders are considered. | WSPL |
| Cyber Security Engineer | provides input to the security planning and risk assessment pertaining to operations and systems administration. | WSPL |
| IT Security Manager | Prepares cybersecurity security plan | WSPL |
| Cyber security consultant | Perform risk assessment to determine the level of risk the system is exposed to, review the cybersecurity plan for completeness, and ensure compliance with relevant cybersecurity standards and regulations. | 3rd Party |
| Users | Approval of cybersecurity plan Provides input to the risk assessment on threats and risk pertaining to business operations. | PUB |

Table 4 Roles and Responsibilities for Security Planning and Risk Assessment

## Critical Security Design Review

| Roles | Responsibilities | Company |
| --- | --- | --- |
| Project Manager | The Project Manager is responsible to ensure that the ITSM has the resources and documentation required in order to perform adequate security review of the system and security architecture. | WSPL |
| IT security manager | Provides inputs to the security review of the system & security architecture | WSPL |
| Cyber security Consultant | The consultant is responsible to perform a security review of the system & security architecture with inputs from stakeholders. | 3rd Party |
| Users |  | PUB |

Table 5 Roles and Responsibilities for Security Design Review

## System Security Acceptance Test

| Roles | Responsibilities | Company |
| --- | --- | --- |
| Project Manager | The Project Manager is responsible to ensure that System Security Acceptance Test Testing is performed adequately | WSPL |
| System Engineer | perform the Systems Security Acceptance Testing. | WSPL |
| IT Security Manager | Plan and perform the Systems Security Acceptance Testing. | WSPL |
| Cyber Security Consultant | Provide independent guidance and verification of SSAT procedures and results. | 3rd Party |
| Users | Participate in validation, provide feedback, and approve test outcomes. | PUB |

Table 6 Roles and Responsibilities for System Security Acceptance Test

## Vulnerability Assessment and Penetration Testing

| Roles | Responsibilities | Company |
| --- | --- | --- |
| Project Manager | Ensure VAPT is conducted by certified personnel. Oversee mitigation planning and ensure follow-up actions are tracked. | Willowglen |
| Cyber Security Engineer | Assist with vulnerability remediation and technical response based on the VAPT report. | Willowglen |
| IT Security Manager | Coordinate and track risk mitigation activities. Facilitate communication with PUB for risk acceptance, if needed. | Willowglen |
| Penetration Tester | Conduct hands-on Vulnerability assessment, penetration testing, exploit vulnerabilities, and prepare technical findings and recommendations. | 3rd Party |
| Cyber Security Consultant | Support VAPT planning, validate scope, and confirm completeness of testing and mitigation. | 3rd Party |
| Users | Review VAPT results, approve risk treatment actions, and endorse risk acceptance where applicable. | PUB |

Table 8 Roles and Responsibilities for VAPT

## Patch and Vulnerability Management

| Roles | Responsibilities | Company |
| --- | --- | --- |
| Project Manager | The Project Manager is responsible to ensure patch management process and procedure are in place, resources are allocated for patch management. | WSPL |
| System Engineer | Performs patch test, implements system patches, | WSPL |
| IT Security Manager | ITSM will - prepare patch management plan for the system, monitor published CVE and CSA SingCERT alert - Identify affected system services / components and prepare mitigation plan - Track CVE / mitigation records, update asset inventory list and patching record - Communicate with end user for the CVE impact, mitigation plan and status | WSPL |
| Users |  | PUB |

Table 7 Roles and Responsibilities for Patch and Vulnerability Management

## Cybersecurity Design requirements

### Asset Management

Asset management includes creating and maintaining a comprehensive inventory of all WSN assets, including hardware, software, assets’ dependencies, and connections with any systems or networks. This is a key component in ensuring cybersecurity as it provides visibility of WSPL assets and allows operators to make informed decisions and prioritise assets for protection. In addition, changes to WSPL asset or information recorded needs to be updated in the asset inventory in a timely manner to ensure that inventory is up to date.

The WSPL shall establish mechanisms and processes to identify all WSN assets and maintain an inventory of the assets. The inventory shall include the following:

- Name/Description of each asset

- Name and Description of critical functions of each asset

- Key person(s) responsible for the cybersecurity of each asset

- Dependencies of each asset and the connections between each asset and any systems or networks (whether internal or external to the system)

- Physical location of each asset

- Information of vendor support of each CII asset

- Inventory of software used in the environment and versioning

- System network topology diagram, including the local network perimeter, and all external computers and computer systems that the system interfaces with

- Software / Firmware version

- Owner and/or operator of each asset

### Account Management

Account management involves the structured creation, monitoring, maintenance, and retirement of user, service, system, and application accounts to ensure secure access and reduce the risk of unauthorized activity.

WSPL shall implement centralized account management services using Active Directory (or an equivalent identity management platform) to manage the entire user account lifecycle. This includes the enforcement of security and hardening configurations on endpoint devices (e.g., Windows computers and servers), centrally governed by the Domain Controller to ensure consistency and compliance across all systems.

Accounts must be managed according to their specific operational needs and associated cybersecurity risks. Overprovisioned and unnecessary privileges must be avoided, and proper controls shall be in place to detect and respond to unauthorized activities.

WSPL shall ensure the following controls are implemented:

- (a) Least Privilege Access: Grant each account only the minimum privileges necessary for its assigned functions and roles.

- (b) Controlled Installation Rights: Ensure that the ability to install software is restricted to accounts authorized to do so.

- (c) Avoid Shared Accounts: Shared user accounts shall not be created unless strictly necessary and justified.

- (d) Activity Monitoring: Monitor account activities, including behavioural patterns, and trigger alerts in the event of anomalies or suspicious behaviour.

- (e) Account Deactivation: Disable or delete accounts that are no longer needed, are inactive, or pose a potential security risk.

- (f) Periodic Account Review: Review all accounts at least once every 12 months to ensure validity and appropriate privilege levels. The first review shall be completed no later than 12 months after the Compliance Date.

### Password Policy

Strong password management and secure user session control shall be implemented across all systems. Where password-based authentication is used, the following enforcement rules shall apply, wherever technically feasible:

- Account Lockout: Account lockout or rate-limiting shall be enforced after a predefined number of failed login attempts. Different thresholds may be configured based on user roles or risk levels.

- Secure Storage: Passwords shall not be stored in plaintext. All passwords must be protected using one-way hashing algorithms with a unique salt value applied before hashing to enhance security.

- Initial Login Password Change: Users shall be required to change their password upon first login. Passwords must be known only to the respective user. No system shall permit the viewing or retrieval of stored passwords.

- Expiry Notification: Users shall be notified 14 days before password expiration to allow timely updates.

- Password Expiry: Standard user passwords shall expire every 90 days, privileged accounts every 30 days, and service accounts every 12 months.

- Strong Password Requirements: Passwords shall be sufficiently strong to resist guessing and brute-force attacks. They must be a minimum of twelve (12) characters in length and include a combination of uppercase letters, lowercase letters, numbers, and special characters.

- Password History: Users are prohibited from reusing any of their last 3 passwords.

### Access Control

Access control is a critical component in protecting WSN assets from unauthorized access. In compliance with the WSCP and aligned with Zero Trust principles, WSPL implements strict role-based access, authentication mechanisms, and access monitoring to safeguard critical infrastructure.

WSPL will implement the following access control measures:

- Role-Based Access Control (RBAC): Access permissions are assigned based on users’ job functions and responsibilities. Each user shall be given the minimum privileges required to perform their duties. The SCADA system shall include the following predefined roles, with configurable levels of access:

| Role | Function |
| --- | --- |
| Guest | View-only access |
| Operator | Control mode changes, manual control, alarm acknowledgement/resetting |
| Shift Supervisor / Lead Op | All operational functions, alarm enable/disable |
| Engineer | Loop tuning, SCADA server maintenance, simulation testing |
| System Administrator | Full system supervision, account management |
| ChE / PM / GM | Audit System Administrator access |
| Contractor | Development/troubleshooting (excluding Operator role) |

- Multi-Factor Authentication (MFA): MFA will be enforced to strengthen user authentication, requiring multiple factors such as passwords, security tokens, or biometric verification before granting access.

- Regular Access Reviews: Periodic audits and reviews will be conducted to validate that user access aligns with current job functions. Any unnecessary or outdated access rights will be promptly revoked.

- Least Privilege Principle: The principle of least privilege will be applied to limit access to the minimum level required for users to perform their tasks, reducing the risk of misuse or compromise.

### Privileged Access

Privileged accounts on a network are prime targets for malicious exploitation because they typically grant higher authority and broader resource access. An attacker who gains control of these accounts could move laterally across the network, access sensitive data, or obtain persistent control of critical systems. Consequently, privileged access requires strict governance, enhanced monitoring, and centralized management to mitigate these risks effectively.

WSPL shall:

- Grant Limited Privileged Access – Only selected, authorized accounts shall receive administrative privileges based on job responsibilities and the principle of least privilege.

- Maintain an Updated Inventory – A continuously updated list of privileged accounts with permissions and assigned roles shall be maintained.

- Implement Multi-Factor Authentication (MFA) – MFA shall be mandatory for all privileged accounts during login and privilege escalation events.

- Use a Privileged Access Management (PAM) System – The PAM system shall:

  - Vault credentials securely in an encrypted repository

  - Enforce MFA at session initiation

  - Monitor and record sessions for audit and anomaly detection

  - Support access approval workflows and just-in-time privilege elevation

- Harden Administrative Environments – Privileged sessions shall only originate from cybersecurity-hardened endpoints, using authorized and encrypted communication channels.

### Zero Trust framework

WSPL shall implement a Zero Trust Architecture (ZTA) across the WSN SCADA and Telemetry System in alignment with PUB’s Water Sector Cybersecurity Policy (WSCP) and the Cybersecurity Code of Practice (CCoP). This approach eliminates implicit trust, enforces least privilege access, and continuously validates identities, devices, and services.

The following control measures shall be implemented:

- Identity and Access Management (IAM):

- Centralized IAM will govern user authentication and access provisioning. All access to critical systems shall require Multi-Factor Authentication (MFA), particularly for administrative and privileged accounts.

- Least Privilege Enforcement:

- Access permissions shall be based strictly on user roles and operational responsibilities. All system functions shall be segregated according to predefined roles, with periodic reviews to validate appropriateness.

- Micro-Segmentation:

- Network architecture shall be segmented into distinct security zones, with inter-zone communications restricted to minimum required functions. All cross-zone traffic shall be inspected and logged.

- Privileged Access Governance:

- Privileged access shall be granted only through controlled workflows, including access approval, session monitoring, and credential vaulting. All privileged sessions must originate from secured and hardened endpoints.

- Continuous Monitoring and Audit Logging:

- System and user activities shall be continuously monitored. All authentication, access, and configuration actions shall be logged centrally and reviewed for anomalies.

- Secure Remote Access:

- Remote access shall be disabled by default. If required, remote sessions shall be time-bound, role-based, and subject to full session logging and access control enforcement.

- Encrypted Communications:

- All data transmissions between users, systems, and network zones must use strong encryption to ensure confidentiality and integrity.

### Remote Access

Remote access refers to the ability to connect to internal systems through an external network. Due to its exposure risk, WSPL ensures remote access is disabled by default. If remote access is required, strict cybersecurity controls will be enforced to maintain the security and integrity of connected systems.

WSPL shall ensure:

- Remote access is granted only to privileged accounts, on an on-demand, pre-approved, and time-limited basis.

- All remote privileged access must go through the privileged access management system.

- Remote sessions are logged and monitored, and session integrity is ensured.

- Remote connections are disabled by default, enabled only when necessary for operations.

- Connections must use strong encryption and pass through secure, intermediary mechanisms.

- Transmission security and message integrity must be enforced over all remote connections.

- All uploaded files must be scanned for malware before being transferred to the system.

- Data flows must be limited to the minimum necessary to perform the intended function.

.

### Network Segmentation

Network segmentation is the separation of a network into different segments based on their security and risk levels, and controlling communication between them. By using data flow control devices or solutions at network intersections and limiting traffic allowed into and out of any given segment, network segmentation makes it difficult for a cyber threat actor to traverse the entire network to perform malicious activities such as reconnaissance work and data theft.

WSPL shall segment its network architecture into distinct zones or segments according to the varying security and risk levels in compliance with WSCP. Communication between network segments shall be strictly limited to the minimum necessary for operational functionality.

WSPL will review the current network architecture and design an effective network segmentation plan that includes the following:

- Defining Security Zones: Establishing distinct network segments or security zones based on the sensitivity of data, system functions, and user roles.

- Securing Inter-Segment Communications: Ensuring secure communication between segments through encryption, access control policies, firewall enforcement, and traffic filtering to prevent unauthorized access or data leakage.

- Implementing Traffic Monitoring and Logging: Deploying mechanisms to monitor and log traffic between segments for anomaly detection and threat identification.

- Perimeter Firewall Enforcement: Deploy perimeter firewalls for communication between SCADA systems across different zones or networks. The firewall shall be a Layer 7 application-capable device, built on a hardened operating system, and must support SCADA-specific protocols such as DNP3 and Modbus. It shall also be capable of forwarding logs to a Syslog server.

### Network security

Network security measures are implemented to control and monitor traffic between different trust domains such as internal organizational networks and external networks, in order to protect against unauthorized access, breaches, and cybersecurity threats. In addition to securing the network perimeter, internal trust boundaries must also be identified and managed to prevent lateral movement and ensure secure access within the environment.

WSPL shall establish a robust and modern network security architecture incorporating the principles of Zero Trust, where no user, device, or application is inherently trusted, even within the internal network.

Key security controls include:

- Zero Trust Architecture: Adopt a Zero Trust approach by enforcing strict identity verification, least-privilege access, and continuous validation of user and device trustworthiness. This includes micro-segmentation of networks and ongoing access monitoring to prevent unauthorized lateral movement.

- Access Control & Network Devices: implement centralized user authentication, role-based authorization, and comprehensive activity logging for all critical network infrastructure (e.g., switches, routers, firewalls). These controls ensure that only authorized personnel can access administrative functions, with permissions aligned to their responsibilities and all access activities recorded for auditing and security monitoring purposes.

- Intrusion Detection and Prevention Systems (IDPS): Deploy IDPS solutions to detect, log, and block suspicious or malicious activity in real time. These systems enhance visibility and provide early warning of potential cyber threats.

- Firewall and Network Segmentation: Configure firewalls to enforce traffic control policies between network zones, prevent unauthorized access, and restrict unnecessary communication paths. Unidirectional data flow (one-way communication) shall be enforced where operationally required, such as between OT and IT zones.

- Secure Communications: All data in transit must be encrypted using secure protocols such as TLS or IPsec to maintain confidentiality and integrity.

- External Network Restrictions: Limit external network connectivity to only those cases deemed operationally necessary. WSPL shall ensure that no system is connected to any network outside the designated secure zone unless explicitly approved and justified.

- Switch Port Security: Network access at the switch level shall be restricted to authorized MAC addresses through port whitelisting, in alignment with system hardening policies.

### Data Security

To protect the confidentiality, integrity, and availability of sensitive and operational data, WSPL shall implement appropriate data security controls across all systems and environments. These controls ensure that data is securely stored, transmitted, and accessed in accordance with cybersecurity best practices and organizational requirements.

The following measures shall be enforced:

- Data Classification and Handling - All data shall be classified based on sensitivity (e.g., confidential, internal, public). Handling procedures should be defined to ensure appropriate protection levels for each data category.

- Data Encryption - Sensitive data shall be encrypted:

  - At rest, using secure encryption algorithms such as AES-256.

  - In transit, using secure communication protocols such as TLS or IPsec.

- Access Control - Access to data shall be limited based on user roles and the principle of least privilege. All access to sensitive files or databases shall be logged and monitored.

- Data Loss Prevention (DLP) - Where applicable, DLP mechanisms shall be implemented to detect and prevent unauthorized data transfers via endpoints, email, or removable media.

- Backup and Recovery - Critical data shall be backed up regularly and stored securely. Backup integrity shall be tested periodically to ensure recovery capability.

### Endpoint Security

To mitigate the risk of endpoint-based threats and unauthorized access, WSPL shall implement strong security controls for all computing endpoints, including engineering workstations, HMIs, laptops, and administrative devices.

The following controls shall be applied:

- Antivirus and Anti-Malware Protection - All endpoints shall be equipped with up-to-date antivirus and anti-malware software (e.g., SEP) with real-time protection and scheduled scans enabled.

- Endpoint Detection and Response (EDR) - EDR solutions shall be deployed to detect, investigate, and respond to suspicious or malicious activities at the endpoint level.

- Patch Management - Endpoints should be updated regularly with security patches and software updates to address known vulnerabilities.

- Endpoint Hardening - Unnecessary applications, services, and ports shall be disabled. Local administrative privileges shall be limited to authorized personnel only.

- Removable Media Control - The use of USB and other removable storage devices shall be restricted. Controls shall be in place to detect and block unauthorized devices.

- Monitoring and Logging - Endpoint events shall be logged and integrated into the centralized SIEM platform to enable threat detection and forensic analysis.

### Application Security

Application-level security controls shall be implemented in accordance with WSCP and CCoP requirements to safeguard WSN critical infrastructure systems.

1. Approved Application List

- WSPL shall establish and maintain a list of approved applications required for the operation and cybersecurity of the CII.

2. Application Whitelisting

- WSPL shall implement application whitelisting through a documented change management process.

- Any non-whitelisted or unnecessary applications on SCADA or other CII systems shall be disabled or removed.

3. Application Integrity Verification

- Prior to deployment or installation, the integrity of all applications shall be verified.

- Verification methods may include checking the file name, extension, version, size, and validating hash values or digital signatures.

4. Application Monitoring and Session Control

- Application Logging: User activities, errors, and critical events within applications shall be logged and integrated with the central SIEM for continuous monitoring.

- Session Management: Systems shall enforce session timeout policies and automatic logout after a defined period of inactivity to prevent unauthorized use.

### Physical Security

WSPL shall implement robust physical security controls to prevent unauthorized access, tampering, or theft of critical infrastructure components, including servers, network devices, field controllers, and operator terminals.

The following physical security measures shall be enforced:

- Perimeter Security: Closed-Circuit Television (CCTV) systems shall be installed to monitor facility entrances, external perimeters, and restricted areas. Footage shall be recorded and retained in accordance with security policy for auditing and incident review purposes.

- Restricted Access to Control Server Rooms: Physical access to sensitive areas such as control server rooms shall be restricted to authorized PUB personnel only. Non-PUB personnel, including System Integrators (SI), shall only access these areas under escort by a PUB officer. Entry shall be controlled using secured mechanisms such as biometric or card-based access systems, with all access attempts logged for audit.

3. Equipment Protection:

- Secured Equipment Racks: All equipment racks shall be locked or sealed to prevent unauthorized tampering or removal of components.

- RJ45 Port Security: All unused RJ45 ports shall be physically blocked with jack lock-out devices. Removal tools shall be retained only by authorized personnel to prevent rogue device insertion.

4. Visitor Access Management: All visitors requiring access to critical or secured areas must be pre-registered and approved. Temporary access is granted only upon valid justification and must be accompanied by an authorized PUB officer throughout the visit.

### System Hardening

In a typical environment, systems comprise various components such as servers, consoles, workstations, appliances, network devices, and field equipment. These systems, in their default configurations, are often not securely configured. Unnecessary services, applications, and open ports may remain active, increasing the risk of exploitation by cyber threat actors.

To reduce the likelihood of system compromise, WSPL shall implement comprehensive system hardening measures to minimize the attack surface and improve the security posture of all project-related assets.

WSPL shall establish and implement security configuration baselines for the following asset types, proportionate to their cybersecurity risk profiles:

- (a) Operating systems

- (b) Appliances

- (c) Consoles and workstations, including Human Machine Interfaces (HMIs) and OT engineering workstations

- (d) Network devices

- (e) Servers, including alarm servers, OT historians, and management servers

These baselines shall follow the guidelines and checklists provided by PUB, ensuring alignment with PUB’s cybersecurity requirements and expectations.

The security configuration baselines shall, at a minimum, address the following controls:

- Account Management – Disable or remove all default, guest, inactive, and unused accounts to reduce unauthorized access risk.

- Password and Passphrase Management – Change all default passwords and store passwords/passphrases using secure one-way hashing algorithms with salting.

- Application Control – Remove or disable all non-essential software, services, and applications not required for operational use.

- Port and Service Management – Only enable network ports and services essential to the operation of the system. Disable all unused or insecure protocols (e.g., SMBv1, Telnet, FTP). Where necessary services (e.g., SMBv2/v3, RDP) are required, they shall be hardened and access controlled.

- Physical Connectivity – Disable all unused physical ports and interfaces.

- Switch Port Whitelisting – All switches shall be configured to allow communication only with known and approved MAC addresses (port security). Switch port whitelisting configurations shall be documented and managed as part of the overall configuration report.

- Malware Protection – Install and maintain up-to-date anti-malware solutions on all applicable endpoints, ensuring real-time protection and regular signature updates.

- Software Updates and Patch Management – Ensure timely application of all critical software and firmware patches to reduce known vulnerabilities.

WSPL shall carry out and verify all system hardening activities based on the defined security configuration baselines prior to any testing phase, including both pre-deployment and installed on-site equipment.

To maintain baseline effectiveness, WSPL shall review and update the security configuration baselines at least once every twelve (12) months. The first review shall be completed within twelve (12) months from initial establishment.

Only authorized computing devices shall be used for the administration of systems and assets. These devices must be restricted solely to administrative functions and shall not be used for non-administrative purposes.

##### Patch and Vulnerability Management

Purpose and Scope
This section describes how WSPL monitors, obtains, tests, and deploys security patches for the Supervisory Control and Data Acquisition (SCADA), telemetry systems, and other critical infrastructure components. The goal is to address vulnerabilities promptly to maintain security and reliability within the WSN environment.

Windows Long-Term Service Channel (LTSC)
WSPL shall provide Windows LTSC operating systems for user computers and servers to ensure extended support cycles and fewer disruptive updates. This approach reduces security risks associated with frequent OS changes.

- Patch Monitoring and Notifications

- Proactive Tracking: WSPL continuously observes vendor releases for new patches or advisories.

- Weekly/Monthly Vulnerability Checks: A Weekly/monthly review of newly published vulnerabilities and advisories is conducted to determine applicability.

- PUB Advisories: Any advisories issued by the Board (PUB) are integrated into WSPL’s patching schedule.

- Vulnerability and CVE Management

- CVE and SingCERT Alert Monitoring: WSPL continuously monitors global CVEs and CSA SingCERT alerts to identify potential threats affecting internal systems.

- Impact Analysis: Identifies affected system components/services and assesses severity.

- End User Communication: Communicates with stakeholders on CVE impact, mitigation actions, and resolution status.

- Patch Management Process

- Testing and Change Management: All patches are tested in a representative offline environment before production. WSPL confirms that patches are free of malicious code and do not conflict with coexisting software. A change management review is performed, with contingency or rollback plans in place.

- Patch Deployment:

  - Anti-virus scanning is performed on patch files prior to deployment.

  - Approval from the Board is obtained where necessary.

  - Patch installation records are maintained, and the IT asset inventory is updated with the new patch status.

- Severity-Based Timelines:

- Centralized Patch Management
WSPL employs a centralized patch management system for distributing updates to user endpoints, servers, and any other devices within the Critical Information Infrastructure (CII) environment. User computers retrieve patches directly from central patch servers to ensure consistent patch levels across all hosts.

- Unpatchable or EOL Scenarios
If a patch cannot be applied (e.g., End of Life or incompatibilities), WSPL conducts a vulnerability assessment and implements compensating controls. Residual risks are documented and submitted for risk acceptance.

- Documentation and Reporting

- Patch Records: WSPL maintains a log of patch releases, testing results, approvals, and installation timelines.

- Backup and Restoration: Before applying major updates, WSPL takes a backup of relevant systems to enable swift restoration if needed.

- Continuous Tracking: WSPL periodically reviews patch effectiveness and reflects changes in the IT asset inventory.

### Obsolescence Management

Purpose and Scope
Obsolescence Management outlines how WSPL tracks and addresses End of Service (EOS) and End of Life (EOL) for hardware and software. The objective is to avoid security gaps posed by unsupported or outdated technologies.

  - EOL/EOS Asset Tracking

- IT Asset Inventory: WSPL includes EOS/EOL dates in its inventory, obtained directly from vendors or official sources.

- Quarterly Review: WSPL shall perform a quarterly review of all equipment, software, and systems to assess lifecycle status, vendor support availability, and potential obsolescence risks. Supporting documentation (e.g., OEM/vendor letter or certification) shall be gathered to justify any refresh or risk mitigation recommendations.

- Annual Review: At least once a year, WSPL reviews the entire hardware/software list for upcoming or actual EOS/EOL status.

  - Obsolescence Report

- Annual Submission: WSPL prepares and submits an Obsolescence Management Report to the Board, highlighting any hardware or software nearing or past end of service.

- Recommendations: The report suggests potential upgrades, replacements, or compensating controls, complete with timelines and projected impacts.

  - Evaluating Updates/Upgrades

- Feasibility: Each year, WSPL examines whether it can safely upgrade to more secure versions of software/hardware.

- Implementation: Upgrades or replacements are carried out as part of maintenance, unless a formal waiver is approved by the Board.

  - Mitigation for Non-Upgradeable Assets

- Risk Assessment: For assets that cannot be updated, WSPL performs a risk assessment and proposes mitigation strategies (e.g., network isolation).

- Risk Acceptance: If mitigation is insufficient, WSPL requests risk acceptance from the Board.

  - Record-Keeping and Compliance

- Change Logs: All obsolescence-related changes or compensations are documented in WSPL’s change management process.

- Audit Readiness: Evidence of compliance, such as upgrade schedules or vendor letters confirming EOL, is maintained and can be provided to auditors or the Board upon request.

### Logging

Logging is the process of recording events occurring within a system or network and enables an organisation to perform investigations and threat hunting. For an organisation to establish and maintain successful log management activities, it is vital that polices are developed based on defined goals and requirements, including the logging scope and log generation, transmission, storage, retention and analysis.

WSPL shall generate, collect and store logs of the following:

- User and Access Activities:

- All user login and logout attempts (successful and failed)

- Actions taken during sessions, including application/database access

- Use of privileged accounts or administrative functions

- Network Logs:

- Internal network connections between system components

- External network connections and remote access sessions

- Firewall traffic logs and policy violations

- DNS query and resolution logs

- System and Service Events:

- Configuration changes and administrative actions

- System startup, shutdown, and service restarts

- Backup and recovery operations

- System monitoring logs (e.g., Sysmon logs for process and activity tracking)

- Database and Field Controller Logs
Where supported, WSPL shall configure SCADA databases and field equipment (e.g., RTUs, PLCs) to save local logs for important operational and security-related events.

- Log Management and Retention
Logs shall be securely stored, protected from unauthorized access or tampering, and retained for an appropriate duration to support system monitoring, incident investigation, and audit requirements.

## Security Acceptance Test

System Security Acceptance Test (SSAT) shall be planned and conducted during the development, installation, and commissioning phases.

The objective of SSAT is to ensure compliance with the Contract Specifications and IEC 62443 standards.

An SSAT plan shall be prepared and submitted to PUB for approval prior to execution. SSAT shall be completed before VAPT.

## Recovery

### Backup and Restoration Plan

A sound backup and restoration plan is critical to protect assets against data loss, corruption, or system disruption. Backup copies of data, configurations, and system components ensure that operations can resume quickly in the event of an incident. To meet regulatory requirements and align with WSCP, the following practices shall be implemented:

- WSPL shall establish and maintain a documented backup and restoration plan to ensure recoverability of critical systems and data. The plan shall include:

  - Data to be backed up

  - Backup frequency

  - Backup type (e.g., full, incremental, differential)

  - Backup storage locations

  - Authorized personnel with access to the backups

  - Steps for accessing and restoring the backups

  - Backup verification procedures

  - Security measures to protect backups from unauthorized access, modification, and deletion

- WSPL shall perform backups at a frequency aligned with operational requirements, and ensure all backups are completed successfully. In particular:

  - System configurations shall be backed up before and after any configuration changes.

  - Historian data shall be backed up based on defined Recovery Point Objective (RPO).

- All backup data shall be stored on devices that are physically isolated from live systems, not connected to the internet, and separated from the original asset locations. Backups must be safeguarded from unauthorized access, tampering, and deletion.

- WSPL shall conduct restoration testing of backups at least annually, or more frequently if dictated by the asset’s cybersecurity risk profile, to verify that data can be successfully restored.

- The backup and restoration plan shall be reviewed and updated at least once every 12 months to ensure ongoing relevance and effectiveness. The first review shall be completed no later than 12 months from the initial plan establishment.

### BUSINESS CONTINUITY AND DISASTER RECOVERY PLAN

To ensure continuous operation and resilience against cybersecurity disruptions, WSPL shall implement a comprehensive Business Continuity Plan (BCP) and Disaster Recovery Plan (DRP). These plans will ensure the timely recovery of critical systems and services.

- Documented Response and Recovery Procedure
WSPL shall develop and maintain a documented BCP and DRP to respond, recover, resume, and restore business operations to a pre-defined level of performance following disruptions. These plans shall outline resources, services, and activities necessary to ensure the continuity of essential services.

- Cybersecurity Threat Scenarios
The BCP and DRP shall include detailed strategies for handling various cybersecurity threats, such as ransomware attacks, system compromise, and denial-of-service incidents.

- RTO and RPO Definitions
The BCP shall define clear Recovery Time Objectives (RTO) and Recovery Point Objectives (RPO) for critical systems and services to guide recovery prioritization and backup intervals.

- Kerberos-Specific Recovery Testing
As part of disaster recovery readiness, WSPL shall establish and document procedures to recover from a potential compromise of the Kerberos Ticket Granting Ticket (TGT) account used by domain controllers. These procedures shall be reviewed and included in DR test exercises where applicable.

- Annual Testing and Review
The BCP and DRP shall be exercised and validated through simulations at least once every 12 months. The first test must be completed within 12 months of the plan’s initial implementation. Lessons learned shall be recorded and integrated into plan revisions.

- Network Recovery Process
WSPL shall document and maintain a process to restore the CII network infrastructure following cybersecurity-related disruptions, including procedures for re-establishing secure communications, re-authentication, and integrity validation.

- Backup Review and Endorsement
System data backups shall be validated regularly, and a backup status checklist shall be prepared.

- Critical Spare List
WSPL shall maintain and annually review a Critical Spare List for SCADA and associated CII assets. This list shall include essential hardware such as:

  - PLC processors

  - Core network switches or routers

  - UPS units and power components

## Cybersecurity Incident Management

The cybersecurity incident management involves the whole process and technology of handling cyberattacks by hackers or unauthorized users to prevent the organization’s system or sensitive data to meet the cybersecurity requirements. The incident management is to help the cybersecurity team to identify, analyse, response, and mitigation of cybersecurity related issues.

- Security incident management plan: cybersecurity incident plan needs to include the procedures of handling incidents, define the security categories and security levels. The plan needs to have the team, roles, responsibilities, and communication plan.

- Incident response team: establish a dedicated team responsible include members from IT, security, legal, and other departments for incident handling, providing team training on the incident response procedure.

- Crisis Communication Plan: A Crisis Communication Plan shall be developed to ensure timely, accurate, and secure dissemination of information during an incident. This plan shall define internal and external communication protocols, contact lists, escalation paths, message templates, and roles responsible for public or stakeholder communication.

- Incident response methodology: follow industry standard incident handling guide for security incident handing.

- Incident review and postmortem: document and record in root cause analysis, action take, monitor, conduct lesson learn and points to improvement updates after the incident.

Overall, respond and control is very important in the incident management. Only after implementing proper incident management methodology, the information security incidents can only be rectified, and this potentially impact an organization's business operations. Some information needs to remain confidential and some need to have transparency, only a proper communication channel is used, it helps on the security incident management.

## 3rd party Cybersecurity Risk Management

WSPL will follow the below steps for the 3rd party cybersecurity risk management

- Identify and evaluate vendors (services and products) and create an inventory.

- Conduct a risk assessment involving the 3rd party services and products to determine risk potential.

- Have vendors complete risk questionnaires when needed.

- Include cybersecurity clauses for contract negotiations, which includes but not limited:

- Cybersecurity Standards and SLA

- Data Protection

- Cybersecurity Beach Handling

- Right to Audit

- Continues monitoring, which involves:

- Response to critical cyber alerts/events

- Implement vulnerability monitoring and tracking

- Implement SLA compliance tracking

- Conduct risk review following the schedule

# Vulnerability Assessment and Penetration Testing (VAPT)

In WSPL, Vulnerability Assessment and Penetration Testing (VAPT) services to help organizations identify and mitigate security vulnerabilities in their digital assets. VAPT involves a comprehensive evaluation of an organization's IT infrastructure, networks, and applications to identify weaknesses that could be exploited by attackers.

## Vulnerability Assessment

VA will be based on white box testing methodology and perform credentialed VA scans.

During the Vulnerability Assessment phase, WSPL team of security experts use automated and manual techniques to scan and test the client's systems for vulnerabilities. This includes network mapping, system fingerprinting, port scanning, vulnerability scanning, and configuration review. The team then provides a report detailing the identified vulnerabilities, along with recommendations for remediation.

The scope of Vulnerability Assessment Service shall include the below:

- All servers

- All HMI

- All routers, firewall and switches

## Penetration Testing

In the Penetration Testing phase, we simulate a real-world attack on the client's systems to test the effectiveness of existing security controls and identify potential attack vectors. This involves attempting to exploit vulnerabilities found during the Vulnerability Assessment phase, as well as conducting social engineering attacks to assess the effectiveness of the client's security awareness training.

The Penetration Testing will be based on grey box and black box testing methodology and identify all roles that are used in applications. User accounts or each identified role will be created and provisioned for authenticated penetration testing.

The team provides a detailed report on the findings, along with recommendations for improving the client's security posture.

## VAPT Steps

Here are the typical steps involved in a Vulnerability Assessment and Penetration Testing:

- Scoping: The first step is to define the scope of the assessment, including the systems, networks, and applications that will be assessed.

- Information gathering: The VA team gathers information about the target systems and applications to understand how they are configured, what software and services are in use, and what potential vulnerabilities may exist.

- Vulnerability scanning: The next step is to use automated tools to scan the target systems and applications for known vulnerabilities. This may include network scanners, web application scanners, and vulnerability scanners.

- Risk assessment: The VA team assesses the risk associated with each identified vulnerability based on the likelihood of exploitation and the potential impact of a successful attack.

- Reporting: The final step is to compile a report detailing the identified vulnerabilities and associated risks, along with recommendations for remediation.

- Remediation: The organization implements the recommendations provided by the VA team to remediate the identified vulnerabilities and reduce the risk of a successful attack.

- Re-assessment: In some cases, a re-assessment may be necessary to ensure that the vulnerabilities have been properly remediated and that the risk has been reduced to an acceptable level.

## TIMING & FREQUENCY

- Timing: VAPT will be conducted after the Site Acceptance Test (SAT) and before the 30-day Plant Proving/System Operability Test, subject to the Board's approval.

- Frequency: Conducted once per project phase unless additional assessments are requested by the Board.

- Approval: Final scope and schedule will be reviewed and approved by the Board.

Overall, WSPL VAPT services can help organizations proactively identify and address security vulnerabilities before they can be exploited by attackers, thereby reducing the risk of data breaches, system downtime, and other security incidents.

# Appendix A Document List

| SN | Document | Description |
| --- | --- | --- |
| 1 | Cybersecurity Plan | - Define project cybersecurity scope - Plan cybersecurity activities and deliverables - Identify cybersecurity roles and responsibilities required for different cybersecurity activities - Capture cybersecurity design requirements |
| 2 | ICT Asset Inventory List | Capture all devices provided by Willowglen for WSN with the attributes below - device type - make - model - installation location - device name - network zone - IP - firmware version - serial number - warranty information |
| 3 | Security-by-Design (SBD) Checklist | - Checklist tracking compliance to CSA’s SBD lifecycle - Includes roles, risk assessment, milestones, design and acceptance validation. |
| 4 | System Security Design Spec | - System network architecture design includes - Zone and Conduit - IP Design - Data Flow - Firewall Rules - Risk and Countermeasures - Define system external interface - System high availability consideration - User and session management - System hardening, patching, backup / restore - Logging and reporting - Cryptographic |
| 5 | System Security Review Report | Ensure the system security design is reviewed and approved by consultant and PUB |
| 6 | Hardening Standard and Guideline | - Prepare hardening guide for PLC / RTU based on Schneider PLC / RTU Cyber Guide - Collect hardening requirement from PUB for switch, HMIs and Servers |
| 7 | Hardening Report | - Hardening checklist for PLC, RTU, Switch, Firewall, HMIs, Servers |
| 8 | Configuration Report | - Switch / Firewall / Radio Controller configuration details |
| 9 | Switch Port Whitelisting | - Port whitelisting (switch port, MAC address) configured for switches |
| 10 | Patch Record | - The latest available firmware version and release date of all IP devices - The deployed firmware version and deploy date of all IP devices |
| 11 | Patching Method of Statement | - Firmware upgrade procedures of all IP devices |
| 12 | SSAT Plan | - Define test objective, strategy and approach - Define test roles and responsibilities - Define test environment - Define test cases |
| 13 | SSAT Report | - Summarizes test results, outcomes, and compliance status from System Security Acceptance Testing (SSAT) |
| 14 | Security Source Code Review Report | - Documents findings from source code analysis, identifying security flaws and recommendations for remediation |
| 15 | Threat & Risk Assessment Report | - Assesses system-level threats, likelihood, and impact, with proposed mitigation controls |
| 16 | VAPT Method of Statement (MOS) | - Outlines approach and methodology for conducting Vulnerability Assessment and Penetration Testing |
| 17 | VAPT Report | - Provides findings, exploited vulnerabilities, risk ratings, and mitigation actions from VAPT activities |
| 18 | Incident Response Plan | - Define procedures of handling incidents - Define the security categories and security levels. - Define the IR team, roles, responsibilities, and communication plan |
| 19 | Business Continuity Plan (BCP). | • Plan to maintain essential services during cyber incidents • Define RTO, RPO, critical processes and continuity actions |
| 20 | Disaster Recovery Plan (DRP). | • Technical recovery plan for SCADA and related CII systems • Network recovery, secure communication, integrity validation. |
| 21 | Crisis Communication Plan. | • Communication strategy during cyber incidents • Include contact lists, message templates, and escalation flows. |